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Quote Ref Number [   ]
Integrated pump and tank system
Supply and install in the position shown on the drawings [1 No.] DPT FlyVar integrated break tank and variable-speed booster set, manufactured and supplied by:
Direct Pumps & Tanks Ltd
Unit 12, Soloman Road
Cossall Industrial Estate
Ilkeston, 
Derbyshire, 
DE7 5UA

T:  0115 944 4474
Email:  enquiries@dpandt.co.uk
Web:  directpumpsandtanks.co.uk

Design duty and configuration

The system shall provide a minimum duty of [      ] L/s at [      ] bar at the nominated design point.
The nominal break-tank storage capacity shall be [    ] litres, selected to suit the calculated peak demand and available incoming mains flow.

The unit shall incorporate [single / twin] pump(s), configured for [duty only / duty-standby] operation as applicable.

Where specified, the system shall provide Category 5 backflow protection using a compliant Type AB air gap: [required / not required]

Construction and principal components

The FlyVar shall be supplied as an integrated package comprising a GRP water storage tank and stainless-steel submersible pump arrangement. The tank shall be pre-insulated and provided with a reinforced base, screened vent, overflow and warning pipe connection where applicable, in accordance with the project requirements and current Water Supply (Water Fittings) Regulations.

•  WRAS-approved stainless-steel submersible pump(s).
•  Independent variable-speed inverter control for each pump.
•  Inlet valve controlled by equilibrium valve
•  WRAS-approved pump control vessel complete with isolation and drain valve.
•  Low-water-level pump protection
•  Digital status display providing operating and fault information.
•  Common alarm volt-free contact for connection to the BMS.
•  Integrated electrical control centre for power and control distribution.
•  Insulated GRP break tank with screened ventilation and overflow provisions.
•  Split-tank or access-orientated configuration where required by site constraints.

Testing, commissioning and handover

The complete unit shall be factory assembled and tested before dispatch. Commissioning shall be undertaken by Direct Pumps & Tanks Ltd or an approved commissioning engineer where included within the project scope. A commissioning record shall be provided for inclusion within the operation and maintenance manual. Warranty shall be in accordance with the Direct Pumps & Tanks Ltd quotation and published terms.
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